## Slide 1: RA workshop presentation
Karl Meeusen, Ph.D.
Senior Advisor – Infrastructure Policy
CPUC Resource Adequacy Workshop
February 18, 2016

## Slide 2: Summary of the ISO comments
The ISO recommends the Commission align its resource adequacy program with the ISO’s planning standards and North American Mandatory Standards
  As a NERC-registered entity, the ISO must comply with all Applicable Reliability Criteria under its FERC-approved Transmission Control Agreement
  Local capacity area resource requirements specified in Section 40.3 of the ISO tariff
ISO must maintain local capacity reliability under NERC Planning Event 6 (P6, formerly Category C) contingencies
  Requires sufficient capacity to readjust the system to prepare for the loss of a second transmission element (N-1-1)

## Slide 3: Summary of the ISO comments
Based on requirement to reposition the system within 30 minutes, the ISO has two options:
  By assessing the system and issuing a dispatch instruction and have a response within 20 minutes*
  By dispatching a resource precontingency so as to have sufficient energy available
The ISO has consistently applied these standards in its Local Capacity Technical Studies
  ISO recently issued a clarification to its BPM providing additional details regarding these study parameters
* 10 minutes is used at beginning of contingency. If resources do not respond, the ISO will not meet reliability requirement

## Slide 4: Excerpts from the ISO’s Local Capacity Technical Report
[I]nputs, assumptions and methodology were discussed and agreed to by stakeholders at the 2016 LCT Study Criteria, Methodology and Assumptions Stakeholder Meeting held on October 30, 2014.
Time allowed for manual readjustment: This is the amount of time required for the operator to take all actions necessary to prepare the system for the next contingency. This time should be less than 30 minutes, based on existing CAISO Planning Standards.

## Slide 5: Three scenarios show how ISO can meet NERC requirements for local capacity areas
Scenario assumptions for local capacity area A:
  Multiple transmission lines serve the area
  Import limit is not binding with all transmission in service
  With one transmission line out of service, import is limited by system voltage stability so imports must be reduced within 30 minutes
Scenarios shown:
  All resources are fast response
  All resources are slow response
  Resources are a mix of fast and slow response

## Slide 6: All fast response
Hours in a day
Imports into local capacity area A (MW)
Import limit with all lines in service
Stability limit with one transmission line out of service
30 minutes total (10 for dispatch; 20 for response)
When a line trips, call fast response DR or fast-response gas-fired resources

## Slide 7: All slow response
Hours in a day
Imports into local capacity area A (MW)
Import limit with all lines in service
Stability limit with one transmission line out of service
Slow resources must be dispatched ahead of time so that flows are below the line limit, regardless if a line trips or not
This may mean slow resources are committed in the day-ahead market, regardless of whether contingency occurs or not.

## Slide 8: Combination of fast and slow (more likely)
Hours in a day
Imports into local capacity area A (MW)
Import limit with all lines in service
Stability limit with one transmission line out of service
With a combination of fast and slow resources, slow resources must be dispatched ahead of time while fast response resources are dispatched after a contingency occurs
Dispatch slow resources to get within “range” of fast response
30 minutes total (10 for dispatch; 20 for response)

## Slide 9: Conclusion
NERC reliability criteria require the ISO return the system to precontingency conditions within 30 minutes during a P6 contingency
The ISO local capacity study utilizes resources that can either receive a dispatch instruction and respond in 30 minutes or be dispatched precontingency to respond in 30 minutes
The NERC reliability requirements and the ISO administration of these requirements have not changed for many years
The ISO recommends the Commission align its resource adequacy program with the ISO’s planning standards and North American Mandatory Standards

## Slide 10: Questions?