## Slide 1: Identifying System Needs for Flexible
Karl Meeusen
Senior Advisor – Infrastructure Policy
CPUC Resource Adequacy Workshop
April 5, 2016

## Slide 2: The ISO has identified four flexible capacity needs to address four issues
Three hour net load ramps
Single-hour net load ramps
Upward and downward dispatchable range during low net load periods and the transition between low net load periods and three-hour ramps and
Five-minute upward and downward deviations during the three-hour net load ramps
The existing flexible product adequately addresses first item

## Slide 3: Three hour net load ramps are predicted to increase in 2017 and beyond
Chart: Distribution of daily max 3-hour net load ramps
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Min | 6328.2904 | 6935.6502 | 5083.5372 | 7205.8273 | 5356.7533 | 3558.6625 | 4026.1116 | 3742.7285 | 4715.9691 | 5328.7777 | 8036.1769 | 5721.8352
bottom 10 | 576.4222 | 1240.3461 | 1649.7107 | 637.2565 | 1096.5406 | 1376.3322 | 1022.1862 | 1921.6562 | 1153.4089 | 692.3946 | 1050.9975 | 2274.7093
10 to 20 | 740.7189 | 829.3869 | 1197.5568 | 510.3763 | 803.0569 | 420.263 | 581.4637 | 409.1919 | 538.028 | 1150.4162 | 981.1989 | 1249.2038
20 to 30 | 386.004 | 645.907 | 1023.1746 | 366.9915 | 345.4514 | 329.2525 | 80.4019 | 277.3586 | 660.8521 | 678.774 | 793.9774 | 692.8374
30 to 40 | 712.76 | 47.7079 | 256.9687 | 367.2396 | 529.9691 | 317.3348 | 316.2053 | 239.3918 | 153.0803 | 500.4053 | 376.5657 | 416.892
40 to 50 | 495.9859 | 467.9346 | 522.0409 | 293.848 | 275.2834 | 232.9339 | 171.4083 | 100.3614 | 851.4909 | 239.6254 | 300.2536 | 86.64
50 to 60 | 459.034 | 487.1776 | 188.5599 | 351.5614 | 152.2427 | 365.3091 | 417.3465 | 138.6611 | 132.5195 | 362.5713 | 345.6037 | 269.2721
60 to 70 | 485.3467 | 173.1789 | 531.2301 | 335.8106 | 707.0047 | 339.1656 | 519.1217 | 329.787 | 242.783 | 138.9724 | 644.5757 | 756.7713
70 to 80 | 174.4704 | 190.9313 | 741.9158 | 452.6973 | 416.2314 | 570.0375 | 284.1013 | 188.6752 | 480.2263 | 340.3651 | 240.9399 | 620.027
80 to 90 | 1160.6765 | 174.6871 | 331.653 | 214.5085 | 190.154 | 719.3745 | 167.6577 | 440.3222 | 537.9328 | 351.0167 | 249.5993 | 358.4018
Max | 1449.8407 | 535.8298 | 837.6415 | 1318.2821 | 864.6394 | 1235.7547 | 811.3946 | 506.7983 | 451.977 | 412.517 | 815.4247 | 952.5783
Chart: Forecasted maximum 3-hour net load ramps for 2017
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
 | 12969.5496 | 11728.7375 | 12363.9894 | 12054.3992 | 10737.3269 | 9464.4203 | 8397.3989 | 8294.9321 | 9918.2679 | 10195.8357 | 13835.3132 | 13399.1683
Each segment is 10 percent of the monthly observations (i.e. three days)

## Slide 4: Rapid expansion of behind-the-meter solar is increasing the size of the three-hour net load ramp
Year-over-year forecasted growth of behind the meter solar is similar to the 2016 Flexible Capacity Technical Needs Assessment
The base behind the meter solar differs widely
  2016 Flexible Capacity Technical Needs Assessment total behind the meter solar for 2017 – 1,740 MW
  Total behind the meter solar for 2017 – 5,975 MW
Current accepted treatment for behind the meter solar in Flexible Capacity Technical Needs Assessment
  Incremental behind the meter solar captured in delta solar
  Existing behind the meter solar impacts delta load

## Slide 5: The magnitude of the secondary net load ramps are decreasing
Percent of Base Flexible capacity needed has decreased for previous year’s study
  2016 study
    64 percent non-summer
    87 percent summer
  2017 study
    50 percent non-summer
    71 percent summer
MW Base Flexible capacity needed are either similar or less than 2016 requirements

## Slide 6: Large, single hour ramps make up a significant portion of the overall three-hour net load ramps
Chart: Distribution of daily max 1-hour net load ramps
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Min | 2982.7094 | 2975.8991 | 2358.251 | 2887.7008 | 2339.2363 | 1853.6029 | 1977.7104 | 1868.1051 | 2279.7854 | 2467.7694 | 3381.1421 | 3638.042
bottom 10 | 210.3124 | 562.9592 | 1004.8352 | 392.7998 | 262.7938 | 450.3158 | 387.6949 | 695.587 | 303.2549 | 299.5743 | 827.5978 | 202.9925
10 to 20 | 320.2418 | 263.0531 | 507.1623 | 407.0569 | 310.0805 | 146.4223 | 131.399 | 47.8066 | 311.0369 | 454.9419 | 195.7477 | 313.8843
20 to 30 | 86.5507 | 413.9812 | 115.2011 | 168.0698 | 293.1944 | 158.8053 | 208.0212 | 145.9316 | 376.5706 | 340.1112 | 95.2445 | 190.8595
30 to 40 | 371.3828 | 161.4797 | 35.3607 | 300.2718 | 174.0874 | 98.3776 | 131.5106 | 191.6187 | 223.057 | 172.9191 | 329.9661 | 121.7764
40 to 50 | 20.4618 | 148.6476 | 357.939 | 167.1271 | 87.4106 | 160.358 | 113.4425 | 70.9485 | 93.826 | 123.8215 | 211.6771 | 144.3946
50 to 60 | 175.4227 | 35.5145 | 105.9966 | 108.1421 | 340.3455 | 71.1737 | 63.5477 | 64.4886 | 139.8176 | 164.1326 | 91.7813 | 130.6014
60 to 70 | 72.3357 | 164.8542 | 270.491 | 37.348 | 153.8599 | 138.0957 | 162.5729 | 48.9465 | 126.8004 | 77.2707 | 392.1277 | 217.9971
70 to 80 | 156.4157 | 233.8257 | 78.6757 | 219.434 | 124.5451 | 173.6812 | 223.9139 | 100.9982 | 157.9752 | 240.7603 | 134.9019 | 107.9888
80 to 90 | 324.9103 | 159.6765 | 586.0857 | 164.879 | 158.3684 | 200.3392 | 78.4246 | 246.6526 | 351.6517 | 490.6569 | 168.4649 | 76.4201
Max | 564.4541 | 94.2039 | 290.9613 | 518.7329 | 501.502 | 395.7545 | 966.8665 | 243.4314 | 109.9936 | 448.3178 | 109.1984 | 487.014
Each segment is 10 percent of the monthly observations (i.e. three days)

## Slide 7: Large, single hour ramps make up a significant portion of the overall three-hour net load ramps
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Min | 0.38681 | 0.38858 | 0.36381 | 0.36713 | 0.37389 | 0.3695 | 0.37895 | 0.38511 | 0.38704 | 0.40269 | 0.37171 | 0.38638
0.1 | 0.014295 | 0.01855 | 0.045513 | 0.043165 | 0.015233 | 0.023385 | 0.034483 | 0.031836 | 0.023919 | 0.010506 | 0.033956 | 0.018492
0.2 | 0.0089864 | 0.01621 | 0.010059 | 0.0040298 | 0.015909 | 0.013105 | 0.0053235 | 0.0011388 | 0.0058398 | 0.01093 | 0.0028446 | 0.012149
0.3 | 0.0027263 | 0.0057722 | 0.012858 | 0.010569 | 0.0036576 | 0.030517 | 0.022518 | 0.0058106 | 0.010443 | 0.010611 | 0.011847 | 0.0013163
0.4 | 0.0053304 | 0.0020127 | 0.007389 | 0.015287 | 0.011555 | 0.0056135 | 0.0043688 | 0.009599 | 0.010971 | 0.0090608 | 0.010139 | 0.0019843
0.5 | 0.0048859 | 0.0056234 | 0.017351 | 0.0063605 | 0.0064391 | 0.013587 | 0.035062 | 0.0081993 | 0.012902 | 0.0055839 | 0.0085862 | 0.0052888
0.6 | 0.0089508 | 0.0045073 | 0.0076583 | 0.0069817 | 0.0019824 | 0.0026592 | 0.0039533 | 0.0067009 | 0.011585 | 0.019325 | 0.0061295 | 0.020994
0.7 | 0.019246 | 0.014719 | 0.0045994 | 0.015213 | 0.0080214 | 0.011498 | 0.0022568 | 0.0094895 | 0.010209 | 0.0071109 | 0.0032569 | 0.0064957
0.8 | 0.015831 | 0.0037335 | 0.010795 | 0.005015 | 0.0067898 | 0.014719 | 0.0093085 | 0.0063529 | 0.011709 | 0.019736 | 0.0080919 | 0.016654
0.9 | 0.026125 | 0.011336 | 0.014858 | 0.0073184 | 0.0094835 | 0.037805 | 0.052719 | 0.023921 | 0.01273 | 0.02611 | 0.0035761 | 0.013447
1 | 0.039543 | 0.033228 | 0.067017 | 0.021753 | 0.015456 | 0.059788 | 0.11752 | 0.058651 | 0.062865 | 0.036464 | 0.13064 | 0.16139
Ratio of one hour ramps to three hour ramps – 2017 forecast (PM ramps only)
Each segment is 10 percent of the monthly observations (i.e. three days)

## Slide 8: Rampable resources must be either on-line with low minimum loads or able to start quickly to address net load ramps

## Slide 9: Rampable resources must be either on-line with low minimum loads or able to start quickly to address net load ramps
ISO must have sufficient ramping capacity available to meet net load ramps
  Fast start
  Low Pmin
Transition from over-generation to ramping needs

## Slide 10: Deviations in load, wind, and solar increase the total mileage needed over the three-hour ramp
Chart: 
2017 Forecast: March 13
Max 3-hour net load ramp = 9,194 MW
Total mileage = 17,523 MW

## Slide 11: Durable Flexible RA Proposal
2016-04-05

## Slide 12: The framework modifies the interim solution to create a durable Flexible RA product
1) Keep the interim solution product definition
  LSE’s procure a single 3 hour product to meet a single flexibility requirement
2) Perform a Multi-Dimension Test to Ensure Reliability
  Once resources are shown by LSEs, CAISO can validate the shown portfolio using multiple flexibility criteria
  Tests will be predefined and well understood by all parties
  Conceptually similar to the current process for Local RA
Framework results in a product that will meet CAISO’s flexibility needs with only minimal changes to the interim product

## Slide 13: Application of the framework results in a simple product that will meet multiple flexibility requirements
In this example:
LSE’s will procure and show a single portfolio that meets a 10,000 MW of 3 hour ramp EFC requirement.
CAISO will test the shown portfolio to see if it has the capability to meet 2,000 MW of 15-minute ramp, 4,000 MW of 1 hour ramp, etc.
Deficiencies are cured by additional LSE showing/procurement and/or ISO backstop procurement
  Details of cure process are TBD, but, conceptually similar to the cure process for Local RA effectiveness deficiencies
Multi-Dimensional Test
10,000 MW 3 Hour Ramp
Other Tests
4,000 MW 1 Hour Ramp
2,000 MW 15 Minute Ramp
Bilateral Product

## Slide 14: SCE designed an analysis to verify the 3 hour product will reliably pass the multi-dimensional test
Framework Analysis Methodology*
  Create generation portfolios that satisfy the 3 hour ramping product
  Test the generation portfolios against the multi-dimensional requirements “Does the flexible RA portfolio meet the largest 15-minute ramp, 1 hour ramp, etc.”
  Determine how often a portfolio that satisfies the 3 hour ramping requirement will pass the multi-dimensional test:
  Assumptions: Generation fleet and System Needs from 2014 LTPP; Product definitions the same as the interim solution; Test requirements developed in a similar manner as the interim solution
Test will always pass regardless of generation portfolio selected
Test is expected to pass, but could not be with specific portfolios
Test is not expected to pass, but could be with specific portfolios
Test could never pass with a portfolio that met the product definition

## Slide 15: 3 Hour Product in the 2024 Trajectory LTPP Case 2024 Net Load and Generation Fleet
*Maintaining the three separate categories from the interim solution (Base, Peak, Super Peak Ramping) will guarantee the twice a day, 3 hour ramp, test always passes
 | Month of Year |  |  |  |  |  |  |  |  |  |  | 
Test Metrics | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
5 Minute Ramp |  |  |  |  |  |  |  |  |  |  |  | 
15 Minute Ramp |  |  |  |  |  |  |  |  |  |  |  | 
30 Minute Ramp |  |  |  |  |  |  |  |  |  |  |  | 
1 Hour Ramp |  |  |  |  |  |  |  |  |  |  |  | 
2 Hour Ramp |  |  |  |  |  |  |  |  |  |  |  | 
3 Hour Ramp (Once a Day) |  |  |  |  |  |  |  |  |  |  |  | 
3 Hour Ramp (Twice a Day)* |  |  |  |  |  |  |  |  |  |  |  | 
Test will always pass regardless of generation portfolio selected
Test is expected to pass, but could not be with specific portfolios
Test is not expected to pass, but could be with specific portfolios
Test could never pass with a portfolio that met the product definition

## Slide 16: Summary of Durable Flexible RA Proposal
3 Hour Flexible RA Product Same as Interim Solution
Multi-Dimension Test to Ensure Reliability Conceptually the same as the Local RA process
Framework results in a bilateral product that will meet CAISO’s flexibility needs with only minimal changes to the interim product